## Sizing tool
Sizing tool
Select your parameters below (yellow fields):
| Sizing | Rating [kW] | Load [%] | Runtime [s]
| BoL | 30 | 50 | 27
| (EoL/BoL) | (30-200kW) | (25-100%) | (3-40s)
Suggested solution
| PN | Qty
| P-105000092-002 | 1
| P-105000092-003 | 0 |  |  | Product references
[5 empty] | Part number | Description | Comment
| Details |  |  |  | P-105000092-001 | ESC-A-0x20-EMPTY-BB-400A-24V | Empty cabinet
| Number of strings | 1 |  |  | P-105000092-002 | ESC-A-1x10-XLM62R1137A-R-BB-400A-24V | 1 string cabinet
| Number of capacitor blocks | 10 |  |  | P-105000092-003 | ESC-A-2x10-XLM62R1137A-R-BB-400A-24V | 2 string cabinet
| Load [kW] | 15 |  |  | P-120000030 | CAPAC SUPER MOD 130F 62V 176x173x686mm | Super capacitor block. Already included in P-105000092-002 and P-105000092-003 cabinets
| Available runtime BoL [s] | 103.3
Sizing tool calculates automaticlaly the needed amount of strings, number of cabinets and runtime.
BoL = Beginning of Life
EoL = End of Life
Estimated life for super capacitors:
20 years @ 30C
12 years @ 35C
8 years @ 40C

## Data (hidden)
| Type | kW | Load level [%] | Runtime [s] | Number of strings
| EoL | 30 | 25 | 3 | 1
| BoL | 40 | 50 | 4 | 2
|  | 50 | 75 | 5 | 3
|  | 54 | 100 | 6 | 4
|  | 80 |  | 7 | 5
|  | 100 |  | 8 | 6
|  | 120 |  | 9 | 7
|  | 150 |  | 10 | 8
|  | 160 |  | 11
|  | 200 |  | 12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
Rating+Runtime |  |  | 25 | 50 | 75 | 100 | Load | Rating+Runtime |  |  | 25 | 50 | 75 | 100 | Load
303 | 30 | 3 | 1 | 1 | 1 | 1 | EoL | 303 | 30 | 3 | 1 | 1 | 1 | 1 | BoL
304 | 30 | 4 | 1 | 1 | 1 | 1 | EoL | 304 | 30 | 4 | 1 | 1 | 1 | 1 | BoL
305 | 30 | 5 | 1 | 1 | 1 | 1 | EoL | 305 | 30 | 5 | 1 | 1 | 1 | 1 | BoL
306 | 30 | 6 | 1 | 1 | 1 | 1 | EoL | 306 | 30 | 6 | 1 | 1 | 1 | 1 | BoL
307 | 30 | 7 | 1 | 1 | 1 | 1 | EoL | 307 | 30 | 7 | 1 | 1 | 1 | 1 | BoL
308 | 30 | 8 | 1 | 1 | 1 | 1 | EoL | 308 | 30 | 8 | 1 | 1 | 1 | 1 | BoL
309 | 30 | 9 | 1 | 1 | 1 | 1 | EoL | 309 | 30 | 9 | 1 | 1 | 1 | 1 | BoL
3010 | 30 | 10 | 1 | 1 | 1 | 1 | EoL | 3010 | 30 | 10 | 1 | 1 | 1 | 1 | BoL
3011 | 30 | 11 | 1 | 1 | 1 | 1 | EoL | 3011 | 30 | 11 | 1 | 1 | 1 | 1 | BoL
3012 | 30 | 12 | 1 | 1 | 1 | 1 | EoL | 3012 | 30 | 12 | 1 | 1 | 1 | 1 | BoL
3013 | 30 | 13 | 1 | 1 | 1 | 1 | EoL | 3013 | 30 | 13 | 1 | 1 | 1 | 1 | BoL
3014 | 30 | 14 | 1 | 1 | 1 | 1 | EoL | 3014 | 30 | 14 | 1 | 1 | 1 | 1 | BoL
3015 | 30 | 15 | 1 | 1 | 1 | 1 | EoL | 3015 | 30 | 15 | 1 | 1 | 1 | 1 | BoL
3016 | 30 | 16 | 1 | 1 | 1 | 1 | EoL | 3016 | 30 | 16 | 1 | 1 | 1 | 1 | BoL
3017 | 30 | 17 | 1 | 1 | 1 | 1 | EoL | 3017 | 30 | 17 | 1 | 1 | 1 | 1 | BoL
3018 | 30 | 18 | 1 | 1 | 1 | 1 | EoL | 3018 | 30 | 18 | 1 | 1 | 1 | 1 | BoL
3019 | 30 | 19 | 1 | 1 | 1 | 1 | EoL | 3019 | 30 | 19 | 1 | 1 | 1 | 1 | BoL
3020 | 30 | 20 | 1 | 1 | 1 | 1 | EoL | 3020 | 30 | 20 | 1 | 1 | 1 | 1 | BoL
3021 | 30 | 21 | 1 | 1 | 1 | 1 | EoL | 3021 | 30 | 21 | 1 | 1 | 1 | 1 | BoL
3022 | 30 | 22 | 1 | 1 | 1 | 1 | EoL | 3022 | 30 | 22 | 1 | 1 | 1 | 1 | BoL
3023 | 30 | 23 | 1 | 1 | 1 | 1 | EoL | 3023 | 30 | 23 | 1 | 1 | 1 | 1 | BoL
3024 | 30 | 24 | 1 | 1 | 1 | 1 | EoL | 3024 | 30 | 24 | 1 | 1 | 1 | 1 | BoL
3025 | 30 | 25 | 1 | 1 | 1 | 1 | EoL | 3025 | 30 | 25 | 1 | 1 | 1 | 1 | BoL
3026 | 30 | 26 | 1 | 1 | 1 | 1 | EoL | 3026 | 30 | 26 | 1 | 1 | 1 | 1 | BoL
3027 | 30 | 27 | 1 | 1 | 1 | 1 | EoL | 3027 | 30 | 27 | 1 | 1 | 1 | 1 | BoL
3028 | 30 | 28 | 1 | 1 | 1 | 1 | EoL | 3028 | 30 | 28 | 1 | 1 | 1 | 1 | BoL
3029 | 30 | 29 | 1 | 1 | 1 | 1 | EoL | 3029 | 30 | 29 | 1 | 1 | 1 | 1 | BoL
3030 | 30 | 30 | 1 | 1 | 1 | 1 | EoL | 3030 | 30 | 30 | 1 | 1 | 1 | 1 | BoL
403 | 40 | 3 | 1 | 1 | 1 | 1 | EoL | 3031 | 30 | 31 | 1 | 1 | 1 | 1 | BoL
404 | 40 | 4 | 1 | 1 | 1 | 1 | EoL | 3032 | 30 | 32 | 1 | 1 | 1 | 1 | BoL
405 | 40 | 5 | 1 | 1 | 1 | 1 | EoL | 3033 | 30 | 33 | 1 | 1 | 1 | 1 | BoL
406 | 40 | 6 | 1 | 1 | 1 | 1 | EoL | 3034 | 30 | 34 | 1 | 1 | 1 | 1 | BoL
407 | 40 | 7 | 1 | 1 | 1 | 1 | EoL | 3035 | 30 | 35 | 1 | 1 | 1 | 1 | BoL
408 | 40 | 8 | 1 | 1 | 1 | 1 | EoL | 3036 | 30 | 36 | 1 | 1 | 1 | 1 | BoL
409 | 40 | 9 | 1 | 1 | 1 | 1 | EoL | 3037 | 30 | 37 | 1 | 1 | 1 | 1 | BoL
4010 | 40 | 10 | 1 | 1 | 1 | 1 | EoL | 3038 | 30 | 38 | 1 | 1 | 1 | 1 | BoL
4011 | 40 | 11 | 1 | 1 | 1 | 1 | EoL | 3039 | 30 | 39 | 1 | 1 | 1 | 1 | BoL
4012 | 40 | 12 | 1 | 1 | 1 | 1 | EoL | 3040 | 30 | 40 | 1 | 1 | 1 | 1 | BoL
4013 | 40 | 13 | 1 | 1 | 1 | 1 | EoL | 3041 | 30 | 41 | 1 | 1 | 1 | 1 | BoL
4014 | 40 | 14 | 1 | 1 | 1 | 1 | EoL | 403 | 40 | 3 | 1 | 1 | 1 | 1 | BoL
4015 | 40 | 15 | 1 | 1 | 1 | 1 | EoL | 404 | 40 | 4 | 1 | 1 | 1 | 1 | BoL
4016 | 40 | 16 | 1 | 1 | 1 | 1 | EoL | 405 | 40 | 5 | 1 | 1 | 1 | 1 | BoL
4017 | 40 | 17 | 1 | 1 | 1 | 1 | EoL | 406 | 40 | 6 | 1 | 1 | 1 | 1 | BoL
4018 | 40 | 18 | 1 | 1 | 1 | 1 | EoL | 407 | 40 | 7 | 1 | 1 | 1 | 1 | BoL
4019 | 40 | 19 | 1 | 1 | 1 | 1 | EoL | 408 | 40 | 8 | 1 | 1 | 1 | 1 | BoL
4020 | 40 | 20 | 1 | 1 | 1 | 1 | EoL | 409 | 40 | 9 | 1 | 1 | 1 | 1 | BoL
4021 | 40 | 21 | 1 | 1 | 1 | 1 | EoL | 4010 | 40 | 10 | 1 | 1 | 1 | 1 | BoL
4022 | 40 | 22 | 1 | 1 | 1 | 1 | EoL | 4011 | 40 | 11 | 1 | 1 | 1 | 1 | BoL
4023 | 40 | 23 | 1 | 1 | 1 | 1 | EoL | 4012 | 40 | 12 | 1 | 1 | 1 | 1 | BoL
4024 | 40 | 24 | 1 | 1 | 1 | 1 | EoL | 4013 | 40 | 13 | 1 | 1 | 1 | 1 | BoL
4025 | 40 | 25 | 1 | 1 | 1 | 1 | EoL | 4014 | 40 | 14 | 1 | 1 | 1 | 1 | BoL
4026 | 40 | 26 | 1 | 1 | 1 | 2 | EoL | 4015 | 40 | 15 | 1 | 1 | 1 | 1 | BoL
4027 | 40 | 27 | 1 | 1 | 1 | 2 | EoL | 4016 | 40 | 16 | 1 | 1 | 1 | 1 | BoL
4028 | 40 | 28 | 1 | 1 | 1 | 2 | EoL | 4017 | 40 | 17 | 1 | 1 | 1 | 1 | BoL
4029 | 40 | 29 | 1 | 1 | 1 | 2 | EoL | 4018 | 40 | 18 | 1 | 1 | 1 | 1 | BoL
4030 | 40 | 30 | 1 | 1 | 1 | 2 | EoL | 4019 | 40 | 19 | 1 | 1 | 1 | 1 | BoL
503 | 50 | 3 | 1 | 1 | 1 | 1 | EoL | 4020 | 40 | 20 | 1 | 1 | 1 | 1 | BoL
504 | 50 | 4 | 1 | 1 | 1 | 1 | EoL | 4021 | 40 | 21 | 1 | 1 | 1 | 1 | BoL
505 | 50 | 5 | 1 | 1 | 1 | 1 | EoL | 4022 | 40 | 22 | 1 | 1 | 1 | 1 | BoL
506 | 50 | 6 | 1 | 1 | 1 | 1 | EoL | 4023 | 40 | 23 | 1 | 1 | 1 | 1 | BoL
507 | 50 | 7 | 1 | 1 | 1 | 1 | EoL | 4024 | 40 | 24 | 1 | 1 | 1 | 1 | BoL
508 | 50 | 8 | 1 | 1 | 1 | 1 | EoL | 4025 | 40 | 25 | 1 | 1 | 1 | 1 | BoL
509 | 50 | 9 | 1 | 1 | 1 | 1 | EoL | 4026 | 40 | 26 | 1 | 1 | 1 | 1 | BoL
5010 | 50 | 10 | 1 | 1 | 1 | 1 | EoL | 4027 | 40 | 27 | 1 | 1 | 1 | 1 | BoL
5011 | 50 | 11 | 1 | 1 | 1 | 1 | EoL | 4028 | 40 | 28 | 1 | 1 | 1 | 1 | BoL
5012 | 50 | 12 | 1 | 1 | 1 | 1 | EoL | 4029 | 40 | 29 | 1 | 1 | 1 | 1 | BoL
5013 | 50 | 13 | 1 | 1 | 1 | 1 | EoL | 4030 | 40 | 30 | 1 | 1 | 1 | 1 | BoL
5014 | 50 | 14 | 1 | 1 | 1 | 1 | EoL | 4031 | 40 | 31 | 1 | 1 | 1 | 1 | BoL
5015 | 50 | 15 | 1 | 1 | 1 | 1 | EoL | 4032 | 40 | 32 | 1 | 1 | 1 | 1 | BoL
5016 | 50 | 16 | 1 | 1 | 1 | 1 | EoL | 4033 | 40 | 33 | 1 | 1 | 1 | 2 | BoL
5017 | 50 | 17 | 1 | 1 | 1 | 1 | EoL | 4034 | 40 | 34 | 1 | 1 | 1 | 2 | BoL
5018 | 50 | 18 | 1 | 1 | 1 | 2 | EoL | 4035 | 40 | 35 | 1 | 1 | 1 | 2 | BoL
5019 | 50 | 19 | 1 | 1 | 1 | 2 | EoL | 4036 | 40 | 36 | 1 | 1 | 1 | 2 | BoL
5020 | 50 | 20 | 1 | 1 | 1 | 2 | EoL | 4037 | 40 | 37 | 1 | 1 | 1 | 2 | BoL
5021 | 50 | 21 | 1 | 1 | 1 | 2 | EoL | 4038 | 40 | 38 | 1 | 1 | 1 | 2 | BoL
5022 | 50 | 22 | 1 | 1 | 1 | 2 | EoL | 4039 | 40 | 39 | 1 | 1 | 1 | 2 | BoL
5023 | 50 | 23 | 1 | 1 | 1 | 2 | EoL | 4040 | 40 | 40 | 1 | 1 | 1 | 2 | BoL
5024 | 50 | 24 | 1 | 1 | 2 | 2 | EoL | 4041 | 40 | 41 | 1 | 1 | 1 | 2 | BoL
5025 | 50 | 25 | 1 | 1 | 2 | 2 | EoL | 503 | 50 | 3 | 1 | 1 | 1 | 1 | BoL
5026 | 50 | 26 | 1 | 1 | 2 | 2 | EoL | 504 | 50 | 4 | 1 | 1 | 1 | 1 | BoL
5027 | 50 | 27 | 1 | 1 | 2 | 2 | EoL | 505 | 50 | 5 | 1 | 1 | 1 | 1 | BoL
5028 | 50 | 28 | 1 | 1 | 2 | 2 | EoL | 506 | 50 | 6 | 1 | 1 | 1 | 1 | BoL
5029 | 50 | 29 | 1 | 1 | 2 | 2 | EoL | 507 | 50 | 7 | 1 | 1 | 1 | 1 | BoL
5030 | 50 | 30 | 1 | 1 | 2 | 2 | EoL | 508 | 50 | 8 | 1 | 1 | 1 | 1 | BoL
543 | 54 | 3 | 1 | 1 | 1 | 1 | EoL | 509 | 50 | 9 | 1 | 1 | 1 | 1 | BoL
544 | 54 | 4 | 1 | 1 | 1 | 1 | EoL | 5010 | 50 | 10 | 1 | 1 | 1 | 1 | BoL
545 | 54 | 5 | 1 | 1 | 1 | 1 | EoL | 5011 | 50 | 11 | 1 | 1 | 1 | 1 | BoL
546 | 54 | 6 | 1 | 1 | 1 | 1 | EoL | 5012 | 50 | 12 | 1 | 1 | 1 | 1 | BoL
547 | 54 | 7 | 1 | 1 | 1 | 1 | EoL | 5013 | 50 | 13 | 1 | 1 | 1 | 1 | BoL
548 | 54 | 8 | 1 | 1 | 1 | 1 | EoL | 5014 | 50 | 14 | 1 | 1 | 1 | 1 | BoL
549 | 54 | 9 | 1 | 1 | 1 | 1 | EoL | 5015 | 50 | 15 | 1 | 1 | 1 | 1 | BoL
5410 | 54 | 10 | 1 | 1 | 1 | 1 | EoL | 5016 | 50 | 16 | 1 | 1 | 1 | 1 | BoL
5411 | 54 | 11 | 1 | 1 | 1 | 1 | EoL | 5017 | 50 | 17 | 1 | 1 | 1 | 1 | BoL
5412 | 54 | 12 | 1 | 1 | 1 | 2 | EoL | 5018 | 50 | 18 | 1 | 1 | 1 | 1 | BoL
5413 | 54 | 13 | 1 | 1 | 1 | 2 | EoL | 5019 | 50 | 19 | 1 | 1 | 1 | 1 | BoL
5414 | 54 | 14 | 1 | 1 | 1 | 2 | EoL | 5020 | 50 | 20 | 1 | 1 | 1 | 1 | BoL
5415 | 54 | 15 | 1 | 1 | 1 | 2 | EoL | 5021 | 50 | 21 | 1 | 1 | 1 | 1 | BoL
5416 | 54 | 16 | 1 | 1 | 2 | 2 | EoL | 5022 | 50 | 22 | 1 | 1 | 1 | 1 | BoL
5417 | 54 | 17 | 1 | 1 | 2 | 2 | EoL | 5023 | 50 | 23 | 1 | 1 | 1 | 2 | BoL
5418 | 54 | 18 | 1 | 1 | 2 | 2 | EoL | 5024 | 50 | 24 | 1 | 1 | 1 | 2 | BoL
5419 | 54 | 19 | 1 | 1 | 2 | 2 | EoL | 5025 | 50 | 25 | 1 | 1 | 1 | 2 | BoL
5420 | 54 | 20 | 1 | 1 | 2 | 2 | EoL | 5026 | 50 | 26 | 1 | 1 | 1 | 2 | BoL
5421 | 54 | 21 | 1 | 1 | 2 | 2 | EoL | 5027 | 50 | 27 | 1 | 1 | 1 | 2 | BoL
5422 | 54 | 22 | 1 | 1 | 2 | 2 | EoL | 5028 | 50 | 28 | 1 | 1 | 1 | 2 | BoL
5423 | 54 | 23 | 1 | 1 | 2 | 2 | EoL | 5029 | 50 | 29 | 1 | 1 | 1 | 2 | BoL
5424 | 54 | 24 | 1 | 1 | 2 | 2 | EoL | 5030 | 50 | 30 | 1 | 1 | 1 | 2 | BoL
5425 | 54 | 25 | 1 | 2 | 2 | 3 | EoL | 5031 | 50 | 31 | 1 | 1 | 2 | 2 | BoL
5426 | 54 | 26 | 1 | 2 | 2 | 3 | EoL | 5032 | 50 | 32 | 1 | 1 | 2 | 2 | BoL
5427 | 54 | 27 | 1 | 2 | 2 | 3 | EoL | 5033 | 50 | 33 | 1 | 1 | 2 | 2 | BoL
5428 | 54 | 28 | 1 | 2 | 2 | 3 | EoL | 5034 | 50 | 34 | 1 | 1 | 2 | 2 | BoL
5429 | 54 | 29 | 1 | 2 | 2 | 3 | EoL | 5035 | 50 | 35 | 1 | 1 | 2 | 2 | BoL
5430 | 54 | 30 | 1 | 2 | 2 | 3 | EoL | 5036 | 50 | 36 | 1 | 1 | 2 | 2 | BoL
803 | 80 | 3 | 1 | 1 | 1 | 1 | EoL | 5037 | 50 | 37 | 1 | 1 | 2 | 2 | BoL
804 | 80 | 4 | 1 | 1 | 1 | 1 | EoL | 5038 | 50 | 38 | 1 | 1 | 2 | 2 | BoL
805 | 80 | 5 | 1 | 1 | 1 | 1 | EoL | 5039 | 50 | 39 | 1 | 1 | 2 | 2 | BoL
806 | 80 | 6 | 1 | 1 | 1 | 1 | EoL | 5040 | 50 | 40 | 1 | 1 | 2 | 2 | BoL
807 | 80 | 7 | 1 | 1 | 1 | 1 | EoL | 5041 | 50 | 41 | 1 | 1 | 2 | 2 | BoL
808 | 80 | 8 | 1 | 1 | 1 | 1 | EoL | 543 | 54 | 3 | 1 | 1 | 1 | 1 | BoL
809 | 80 | 9 | 1 | 1 | 1 | 1 | EoL | 544 | 54 | 4 | 1 | 1 | 1 | 1 | BoL
8010 | 80 | 10 | 1 | 1 | 1 | 1 | EoL | 545 | 54 | 5 | 1 | 1 | 1 | 1 | BoL
8011 | 80 | 11 | 1 | 1 | 1 | 2 | EoL | 546 | 54 | 6 | 1 | 1 | 1 | 1 | BoL
8012 | 80 | 12 | 1 | 1 | 1 | 2 | EoL | 547 | 54 | 7 | 1 | 1 | 1 | 1 | BoL
8013 | 80 | 13 | 1 | 1 | 1 | 2 | EoL | 548 | 54 | 8 | 1 | 1 | 1 | 1 | BoL
8014 | 80 | 14 | 1 | 1 | 1 | 2 | EoL | 549 | 54 | 9 | 1 | 1 | 1 | 1 | BoL
8015 | 80 | 15 | 1 | 1 | 2 | 2 | EoL | 5410 | 54 | 10 | 1 | 1 | 1 | 1 | BoL
8016 | 80 | 16 | 1 | 1 | 2 | 2 | EoL | 5411 | 54 | 11 | 1 | 1 | 1 | 1 | BoL
8017 | 80 | 17 | 1 | 1 | 2 | 2 | EoL | 5412 | 54 | 12 | 1 | 1 | 1 | 1 | BoL
8018 | 80 | 18 | 1 | 1 | 2 | 2 | EoL | 5413 | 54 | 13 | 1 | 1 | 1 | 1 | BoL
8019 | 80 | 19 | 1 | 1 | 2 | 2 | EoL | 5414 | 54 | 14 | 1 | 1 | 1 | 1 | BoL
8020 | 80 | 20 | 1 | 1 | 2 | 2 | EoL | 5415 | 54 | 15 | 1 | 1 | 1 | 1 | BoL
8021 | 80 | 21 | 1 | 1 | 2 | 2 | EoL | 5416 | 54 | 16 | 1 | 1 | 1 | 2 | BoL
8022 | 80 | 22 | 1 | 1 | 2 | 2 | EoL | 5417 | 54 | 17 | 1 | 1 | 1 | 2 | BoL
8023 | 80 | 23 | 1 | 2 | 2 | 3 | EoL | 5418 | 54 | 18 | 1 | 1 | 1 | 2 | BoL
8024 | 80 | 24 | 1 | 2 | 2 | 3 | EoL | 5419 | 54 | 19 | 1 | 1 | 1 | 2 | BoL
8025 | 80 | 25 | 1 | 2 | 2 | 3 | EoL | 5420 | 54 | 20 | 1 | 1 | 1 | 2 | BoL
8026 | 80 | 26 | 1 | 2 | 2 | 3 | EoL | 5421 | 54 | 21 | 1 | 1 | 1 | 2 | BoL
8027 | 80 | 27 | 1 | 2 | 2 | 3 | EoL | 5422 | 54 | 22 | 1 | 1 | 2 | 2 | BoL
8028 | 80 | 28 | 1 | 2 | 2 | 3 | EoL | 5423 | 54 | 23 | 1 | 1 | 2 | 2 | BoL
8029 | 80 | 29 | 1 | 2 | 2 | 3 | EoL | 5424 | 54 | 24 | 1 | 1 | 2 | 2 | BoL
8030 | 80 | 30 | 1 | 2 | 2 | 3 | EoL | 5425 | 54 | 25 | 1 | 1 | 2 | 2 | BoL
1003 | 100 | 3 | 1 | 1 | 1 | 1 | EoL | 5426 | 54 | 26 | 1 | 1 | 2 | 2 | BoL
1004 | 100 | 4 | 1 | 1 | 1 | 1 | EoL | 5427 | 54 | 27 | 1 | 1 | 2 | 2 | BoL
1005 | 100 | 5 | 1 | 1 | 1 | 1 | EoL | 5428 | 54 | 28 | 1 | 1 | 2 | 2 | BoL
1006 | 100 | 6 | 1 | 1 | 1 | 1 | EoL | 5429 | 54 | 29 | 1 | 1 | 2 | 2 | BoL
1007 | 100 | 7 | 1 | 1 | 1 | 1 | EoL | 5430 | 54 | 30 | 1 | 1 | 2 | 2 | BoL
1008 | 100 | 8 | 1 | 1 | 1 | 2 | EoL | 5431 | 54 | 31 | 1 | 1 | 2 | 2 | BoL
1009 | 100 | 9 | 1 | 1 | 1 | 2 | EoL | 5432 | 54 | 32 | 1 | 2 | 2 | 2 | BoL
10010 | 100 | 10 | 1 | 1 | 1 | 2 | EoL | 5433 | 54 | 33 | 1 | 2 | 2 | 3 | BoL
10011 | 100 | 11 | 1 | 1 | 2 | 2 | EoL | 5434 | 54 | 34 | 1 | 2 | 2 | 3 | BoL
10012 | 100 | 12 | 1 | 1 | 2 | 2 | EoL | 5435 | 54 | 35 | 1 | 2 | 2 | 3 | BoL
10013 | 100 | 13 | 1 | 1 | 2 | 2 | EoL | 5436 | 54 | 36 | 1 | 2 | 2 | 3 | BoL
10014 | 100 | 14 | 1 | 1 | 2 | 2 | EoL | 5437 | 54 | 37 | 1 | 2 | 2 | 3 | BoL
10015 | 100 | 15 | 1 | 1 | 2 | 2 | EoL | 5438 | 54 | 38 | 1 | 2 | 2 | 3 | BoL
10016 | 100 | 16 | 1 | 1 | 2 | 2 | EoL | 5439 | 54 | 39 | 1 | 2 | 2 | 3 | BoL
10017 | 100 | 17 | 1 | 2 | 2 | 2 | EoL | 5440 | 54 | 40 | 1 | 2 | 2 | 3 | BoL
10018 | 100 | 18 | 1 | 2 | 2 | 3 | EoL | 5441 | 54 | 41 | 1 | 2 | 2 | 3 | BoL
10019 | 100 | 19 | 1 | 2 | 2 | 3 | EoL | 803 | 80 | 3 | 1 | 1 | 1 | 1 | BoL
10020 | 100 | 20 | 1 | 2 | 2 | 3 | EoL | 804 | 80 | 4 | 1 | 1 | 1 | 1 | BoL
10021 | 100 | 21 | 1 | 2 | 2 | 3 | EoL | 805 | 80 | 5 | 1 | 1 | 1 | 1 | BoL
10022 | 100 | 22 | 1 | 2 | 2 | 3 | EoL | 806 | 80 | 6 | 1 | 1 | 1 | 1 | BoL
10023 | 100 | 23 | 1 | 2 | 2 | 3 | EoL | 807 | 80 | 7 | 1 | 1 | 1 | 1 | BoL
10024 | 100 | 24 | 1 | 2 | 3 | 3 | EoL | 808 | 80 | 8 | 1 | 1 | 1 | 1 | BoL
10025 | 100 | 25 | 1 | 2 | 3 | 3 | EoL | 809 | 80 | 9 | 1 | 1 | 1 | 1 | BoL
10026 | 100 | 26 | 1 | 2 | 3 | 3 | EoL | 8010 | 80 | 10 | 1 | 1 | 1 | 1 | BoL
10027 | 100 | 27 | 1 | 2 | 3 | 4 | EoL | 8011 | 80 | 11 | 1 | 1 | 1 | 1 | BoL
10028 | 100 | 28 | 1 | 2 | 3 | 4 | EoL | 8012 | 80 | 12 | 1 | 1 | 1 | 1 | BoL
10029 | 100 | 29 | 1 | 2 | 3 | 4 | EoL | 8013 | 80 | 13 | 1 | 1 | 1 | 1 | BoL
10030 | 100 | 30 | 1 | 2 | 3 | 4 | EoL | 8014 | 80 | 14 | 1 | 1 | 1 | 1 | BoL
1203 | 120 | 3 | 1 | 1 | 1 | 1 | EoL | 8015 | 80 | 15 | 1 | 1 | 1 | 2 | BoL
1204 | 120 | 4 | 1 | 1 | 1 | 1 | EoL | 8016 | 80 | 16 | 1 | 1 | 1 | 2 | BoL
1205 | 120 | 5 | 1 | 1 | 1 | 1 | EoL | 8017 | 80 | 17 | 1 | 1 | 1 | 2 | BoL
1206 | 120 | 6 | 1 | 1 | 1 | 1 | EoL | 8018 | 80 | 18 | 1 | 1 | 1 | 2 | BoL
1207 | 120 | 7 | 1 | 1 | 1 | 2 | EoL | 8019 | 80 | 19 | 1 | 1 | 1 | 2 | BoL
1208 | 120 | 8 | 1 | 1 | 1 | 2 | EoL | 8020 | 80 | 20 | 1 | 1 | 2 | 2 | BoL
1209 | 120 | 9 | 1 | 1 | 2 | 2 | EoL | 8021 | 80 | 21 | 1 | 1 | 2 | 2 | BoL
12010 | 120 | 10 | 1 | 1 | 2 | 2 | EoL | 8022 | 80 | 22 | 1 | 1 | 2 | 2 | BoL
12011 | 120 | 11 | 1 | 1 | 2 | 2 | EoL | 8023 | 80 | 23 | 1 | 1 | 2 | 2 | BoL
12012 | 120 | 12 | 1 | 1 | 2 | 2 | EoL | 8024 | 80 | 24 | 1 | 1 | 2 | 2 | BoL
12013 | 120 | 13 | 1 | 1 | 2 | 2 | EoL | 8025 | 80 | 25 | 1 | 1 | 2 | 2 | BoL
12014 | 120 | 14 | 1 | 1 | 2 | 2 | EoL | 8026 | 80 | 26 | 1 | 1 | 2 | 2 | BoL
12015 | 120 | 15 | 1 | 2 | 2 | 3 | EoL | 8027 | 80 | 27 | 1 | 1 | 2 | 2 | BoL
12016 | 120 | 16 | 1 | 2 | 2 | 3 | EoL | 8028 | 80 | 28 | 1 | 1 | 2 | 2 | BoL
12017 | 120 | 17 | 1 | 2 | 2 | 3 | EoL | 8029 | 80 | 29 | 1 | 1 | 2 | 2 | BoL
12018 | 120 | 18 | 1 | 2 | 2 | 3 | EoL | 8030 | 80 | 30 | 1 | 2 | 2 | 3 | BoL
12019 | 120 | 19 | 1 | 2 | 2 | 3 | EoL | 8031 | 80 | 31 | 1 | 2 | 2 | 3 | BoL
12020 | 120 | 20 | 1 | 2 | 3 | 3 | EoL | 8032 | 80 | 32 | 1 | 2 | 2 | 3 | BoL
12021 | 120 | 21 | 1 | 2 | 3 | 3 | EoL | 8033 | 80 | 33 | 1 | 2 | 2 | 3 | BoL
12022 | 120 | 22 | 1 | 2 | 3 | 3 | EoL | 8034 | 80 | 34 | 1 | 2 | 2 | 3 | BoL
12023 | 120 | 23 | 1 | 2 | 3 | 4 | EoL | 8035 | 80 | 35 | 1 | 2 | 2 | 3 | BoL
12024 | 120 | 24 | 1 | 2 | 3 | 4 | EoL | 8036 | 80 | 36 | 1 | 2 | 2 | 3 | BoL
12025 | 120 | 25 | 1 | 2 | 3 | 4 | EoL | 8037 | 80 | 37 | 1 | 2 | 2 | 3 | BoL
12026 | 120 | 26 | 1 | 2 | 3 | 4 | EoL | 8038 | 80 | 38 | 1 | 2 | 2 | 3 | BoL
12027 | 120 | 27 | 1 | 2 | 3 | 4 | EoL | 8039 | 80 | 39 | 1 | 2 | 2 | 3 | BoL
12028 | 120 | 28 | 1 | 2 | 3 | 4 | EoL | 8040 | 80 | 40 | 1 | 2 | 2 | 3 | BoL
12029 | 120 | 29 | 1 | 2 | 3 | 4 | EoL | 8041 | 80 | 41 | 1 | 2 | 3 | 3 | BoL
12030 | 120 | 30 | 2 | 2 | 3 | 4 | EoL | 1003 | 100 | 3 | 1 | 1 | 1 | 1 | BoL
1503 | 150 | 3 | 1 | 1 | 1 | 1 | EoL | 1004 | 100 | 4 | 1 | 1 | 1 | 1 | BoL
1504 | 150 | 4 | 1 | 1 | 1 | 1 | EoL | 1005 | 100 | 5 | 1 | 1 | 1 | 1 | BoL
1505 | 150 | 5 | 1 | 1 | 1 | 2 | EoL | 1006 | 100 | 6 | 1 | 1 | 1 | 1 | BoL
1506 | 150 | 6 | 1 | 1 | 1 | 2 | EoL | 1007 | 100 | 7 | 1 | 1 | 1 | 1 | BoL
1507 | 150 | 7 | 1 | 1 | 2 | 2 | EoL | 1008 | 100 | 8 | 1 | 1 | 1 | 1 | BoL
1508 | 150 | 8 | 1 | 1 | 2 | 2 | EoL | 1009 | 100 | 9 | 1 | 1 | 1 | 1 | BoL
1509 | 150 | 9 | 1 | 1 | 2 | 2 | EoL | 10010 | 100 | 10 | 1 | 1 | 1 | 1 | BoL
15010 | 150 | 10 | 1 | 1 | 2 | 2 | EoL | 10011 | 100 | 11 | 1 | 1 | 1 | 2 | BoL
15011 | 150 | 11 | 1 | 2 | 2 | 3 | EoL | 10012 | 100 | 12 | 1 | 1 | 1 | 2 | BoL
15012 | 150 | 12 | 1 | 2 | 2 | 3 | EoL | 10013 | 100 | 13 | 1 | 1 | 1 | 2 | BoL
15013 | 150 | 13 | 1 | 2 | 2 | 3 | EoL | 10014 | 100 | 14 | 1 | 1 | 1 | 2 | BoL
15014 | 150 | 14 | 1 | 2 | 2 | 3 | EoL | 10015 | 100 | 15 | 1 | 1 | 2 | 2 | BoL
15015 | 150 | 15 | 1 | 2 | 3 | 3 | EoL | 10016 | 100 | 16 | 1 | 1 | 2 | 2 | BoL
15016 | 150 | 16 | 1 | 2 | 3 | 3 | EoL | 10017 | 100 | 17 | 1 | 1 | 2 | 2 | BoL
15017 | 150 | 17 | 1 | 2 | 3 | 3 | EoL | 10018 | 100 | 18 | 1 | 1 | 2 | 2 | BoL
15018 | 150 | 18 | 1 | 2 | 3 | 4 | EoL | 10019 | 100 | 19 | 1 | 1 | 2 | 2 | BoL
15019 | 150 | 19 | 1 | 2 | 3 | 4 | EoL | 10020 | 100 | 20 | 1 | 1 | 2 | 2 | BoL
15020 | 150 | 20 | 1 | 2 | 3 | 4 | EoL | 10021 | 100 | 21 | 1 | 1 | 2 | 2 | BoL
15021 | 150 | 21 | 1 | 2 | 3 | 4 | EoL | 10022 | 100 | 22 | 1 | 1 | 2 | 2 | BoL
15022 | 150 | 22 | 1 | 2 | 3 | 4 | EoL | 10023 | 100 | 23 | 1 | 2 | 2 | 3 | BoL
15023 | 150 | 23 | 2 | 2 | 3 | 4 | EoL | 10024 | 100 | 24 | 1 | 2 | 2 | 3 | BoL
15024 | 150 | 24 | 2 | 3 | 4 | 5 | EoL | 10025 | 100 | 25 | 1 | 2 | 2 | 3 | BoL
15025 | 150 | 25 | 2 | 3 | 4 | 5 | EoL | 10026 | 100 | 26 | 1 | 2 | 2 | 3 | BoL
15026 | 150 | 26 | 2 | 3 | 4 | 5 | EoL | 10027 | 100 | 27 | 1 | 2 | 2 | 3 | BoL
15027 | 150 | 27 | 2 | 3 | 4 | 5 | EoL | 10028 | 100 | 28 | 1 | 2 | 2 | 3 | BoL
15028 | 150 | 28 | 2 | 3 | 4 | 5 | EoL | 10029 | 100 | 29 | 1 | 2 | 2 | 3 | BoL
15029 | 150 | 29 | 2 | 3 | 4 | 5 | EoL | 10030 | 100 | 30 | 1 | 2 | 2 | 3 | BoL
15030 | 150 | 30 | 2 | 3 | 4 | 6 | EoL | 10031 | 100 | 31 | 1 | 2 | 3 | 3 | BoL
1603 | 160 | 3 | 1 | 1 | 1 | 1 | EoL | 10032 | 100 | 32 | 1 | 2 | 3 | 3 | BoL
1604 | 160 | 4 | 1 | 1 | 1 | 1 | EoL | 10033 | 100 | 33 | 1 | 2 | 3 | 3 | BoL
1605 | 160 | 5 | 1 | 1 | 1 | 2 | EoL | 10034 | 100 | 34 | 1 | 2 | 3 | 3 | BoL
1606 | 160 | 6 | 1 | 1 | 1 | 2 | EoL | 10035 | 100 | 35 | 1 | 2 | 3 | 4 | BoL
1607 | 160 | 7 | 1 | 1 | 2 | 2 | EoL | 10036 | 100 | 36 | 1 | 2 | 3 | 4 | BoL
1608 | 160 | 8 | 1 | 1 | 2 | 2 | EoL | 10037 | 100 | 37 | 1 | 2 | 3 | 4 | BoL
1609 | 160 | 9 | 1 | 1 | 2 | 2 | EoL | 10038 | 100 | 38 | 1 | 2 | 3 | 4 | BoL
16010 | 160 | 10 | 1 | 1 | 2 | 2 | EoL | 10039 | 100 | 39 | 1 | 2 | 3 | 4 | BoL
16011 | 160 | 11 | 1 | 1 | 2 | 2 | EoL | 10040 | 100 | 40 | 1 | 2 | 3 | 4 | BoL
16012 | 160 | 12 | 1 | 2 | 2 | 3 | EoL | 10041 | 100 | 41 | 1 | 2 | 3 | 4 | BoL
16013 | 160 | 13 | 1 | 2 | 2 | 3 | EoL | 1203 | 120 | 3 | 1 | 1 | 1 | 1 | BoL
16014 | 160 | 14 | 1 | 2 | 2 | 3 | EoL | 1204 | 120 | 4 | 1 | 1 | 1 | 1 | BoL
16015 | 160 | 15 | 1 | 2 | 2 | 3 | EoL | 1205 | 120 | 5 | 1 | 1 | 1 | 1 | BoL
16016 | 160 | 16 | 1 | 2 | 3 | 3 | EoL | 1206 | 120 | 6 | 1 | 1 | 1 | 1 | BoL
16017 | 160 | 17 | 1 | 2 | 3 | 3 | EoL | 1207 | 120 | 7 | 1 | 1 | 1 | 1 | BoL
16018 | 160 | 18 | 1 | 2 | 3 | 3 | EoL | 1208 | 120 | 8 | 1 | 1 | 1 | 1 | BoL
16019 | 160 | 19 | 1 | 2 | 3 | 4 | EoL | 1209 | 120 | 9 | 1 | 1 | 1 | 2 | BoL
16020 | 160 | 20 | 1 | 2 | 3 | 4 | EoL | 12010 | 120 | 10 | 1 | 1 | 1 | 2 | BoL
16021 | 160 | 21 | 1 | 2 | 3 | 4 | EoL | 12011 | 120 | 11 | 1 | 1 | 1 | 2 | BoL
16022 | 160 | 22 | 1 | 2 | 3 | 4 | EoL | 12012 | 120 | 12 | 1 | 1 | 1 | 2 | BoL
16023 | 160 | 23 | 1 | 2 | 3 | 4 | EoL | 12013 | 120 | 13 | 1 | 1 | 2 | 2 | BoL
16024 | 160 | 24 | 2 | 2 | 3 | 4 | EoL | 12014 | 120 | 14 | 1 | 1 | 2 | 2 | BoL
16025 | 160 | 25 | 2 | 3 | 3 | 4 | EoL | 12015 | 120 | 15 | 1 | 1 | 2 | 2 | BoL
16026 | 160 | 26 | 2 | 3 | 4 | 5 | EoL | 12016 | 120 | 16 | 1 | 1 | 2 | 2 | BoL
16027 | 160 | 27 | 2 | 3 | 4 | 5 | EoL | 12017 | 120 | 17 | 1 | 1 | 2 | 2 | BoL
16028 | 160 | 28 | 2 | 3 | 4 | 5 | EoL | 12018 | 120 | 18 | 1 | 1 | 2 | 2 | BoL
16029 | 160 | 29 | 2 | 3 | 4 | 5 | EoL | 12019 | 120 | 19 | 1 | 1 | 2 | 2 | BoL
16030 | 160 | 30 | 2 | 3 | 4 | 5 | EoL | 12020 | 120 | 20 | 1 | 2 | 2 | 3 | BoL
2003 | 200 | 3 | 1 | 1 | 1 | 2 | EoL | 12021 | 120 | 21 | 1 | 2 | 2 | 3 | BoL
2004 | 200 | 4 | 1 | 1 | 1 | 2 | EoL | 12022 | 120 | 22 | 1 | 2 | 2 | 3 | BoL
2005 | 200 | 5 | 1 | 1 | 2 | 2 | EoL | 12023 | 120 | 23 | 1 | 2 | 2 | 3 | BoL
2006 | 200 | 6 | 1 | 1 | 2 | 2 | EoL | 12024 | 120 | 24 | 1 | 2 | 2 | 3 | BoL
2007 | 200 | 7 | 1 | 1 | 2 | 2 | EoL | 12025 | 120 | 25 | 1 | 2 | 2 | 3 | BoL
2008 | 200 | 8 | 1 | 2 | 2 | 3 | EoL | 12026 | 120 | 26 | 1 | 2 | 2 | 3 | BoL
2009 | 200 | 9 | 1 | 2 | 2 | 3 | EoL | 12027 | 120 | 27 | 1 | 2 | 3 | 3 | BoL
20010 | 200 | 10 | 1 | 2 | 2 | 3 | EoL | 12028 | 120 | 28 | 1 | 2 | 3 | 3 | BoL
20011 | 200 | 11 | 1 | 2 | 3 | 3 | EoL | 12029 | 120 | 29 | 1 | 2 | 3 | 3 | BoL
20012 | 200 | 12 | 1 | 2 | 3 | 3 | EoL | 12030 | 120 | 30 | 1 | 2 | 3 | 4 | BoL
20013 | 200 | 13 | 1 | 2 | 3 | 4 | EoL | 12031 | 120 | 31 | 1 | 2 | 3 | 4 | BoL
20014 | 200 | 14 | 1 | 2 | 3 | 4 | EoL | 12032 | 120 | 32 | 1 | 2 | 3 | 4 | BoL
20015 | 200 | 15 | 1 | 2 | 3 | 4 | EoL | 12033 | 120 | 33 | 1 | 2 | 3 | 4 | BoL
20016 | 200 | 16 | 1 | 2 | 3 | 4 | EoL | 12034 | 120 | 34 | 1 | 2 | 3 | 4 | BoL
20017 | 200 | 17 | 2 | 3 | 3 | 4 | EoL | 12035 | 120 | 35 | 1 | 2 | 3 | 4 | BoL
20018 | 200 | 18 | 2 | 3 | 4 | 5 | EoL | 12036 | 120 | 36 | 1 | 2 | 3 | 4 | BoL
20019 | 200 | 19 | 2 | 3 | 4 | 5 | EoL | 12037 | 120 | 37 | 1 | 2 | 3 | 4 | BoL
20020 | 200 | 20 | 2 | 3 | 4 | 5 | EoL | 12038 | 120 | 38 | 2 | 2 | 3 | 4 | BoL
20021 | 200 | 21 | 2 | 3 | 4 | 5 | EoL | 12039 | 120 | 39 | 2 | 2 | 3 | 4 | BoL
20022 | 200 | 22 | 2 | 3 | 4 | 6 | EoL | 12040 | 120 | 40 | 2 | 3 | 3 | 4 | BoL
20023 | 200 | 23 | 2 | 3 | 4 | 6 | EoL | 12041 | 120 | 41 | 2 | 3 | 4 | 5 | BoL
20024 | 200 | 24 | 2 | 3 | 5 | 6 | EoL | 1503 | 150 | 3 | 1 | 1 | 1 | 1 | BoL
20025 | 200 | 25 | 2 | 3 | 5 | 6 | EoL | 1504 | 150 | 4 | 1 | 1 | 1 | 1 | BoL
20026 | 200 | 26 | 2 | 3 | 5 | 6 | EoL | 1505 | 150 | 5 | 1 | 1 | 1 | 1 | BoL
20027 | 200 | 27 | 2 | 4 | 5 | 7 | EoL | 1506 | 150 | 6 | 1 | 1 | 1 | 1 | BoL
20028 | 200 | 28 | 2 | 4 | 5 | 7 | EoL | 1507 | 150 | 7 | 1 | 1 | 1 | 2 | BoL
20029 | 200 | 29 | 2 | 4 | 5 | 7 | EoL | 1508 | 150 | 8 | 1 | 1 | 1 | 2 | BoL
20030 | 200 | 30 | 2 | 4 | 6 | 7 | EoL | 1509 | 150 | 9 | 1 | 1 | 1 | 2 | BoL
[8 empty] | 15010 | 150 | 10 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 15011 | 150 | 11 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 15012 | 150 | 12 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 15013 | 150 | 13 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 15014 | 150 | 14 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 15015 | 150 | 15 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 15016 | 150 | 16 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 15017 | 150 | 17 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 15018 | 150 | 18 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 15019 | 150 | 19 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 15020 | 150 | 20 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 15021 | 150 | 21 | 1 | 2 | 3 | 3 | BoL
[8 empty] | 15022 | 150 | 22 | 1 | 2 | 3 | 3 | BoL
[8 empty] | 15023 | 150 | 23 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 15024 | 150 | 24 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 15025 | 150 | 25 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 15026 | 150 | 26 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 15027 | 150 | 27 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 15028 | 150 | 28 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 15029 | 150 | 29 | 2 | 2 | 3 | 4 | BoL
[8 empty] | 15030 | 150 | 30 | 2 | 2 | 3 | 4 | BoL
[8 empty] | 15031 | 150 | 31 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 15032 | 150 | 32 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 15033 | 150 | 33 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 15034 | 150 | 34 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 15035 | 150 | 35 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 15036 | 150 | 36 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 15037 | 150 | 37 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 15038 | 150 | 38 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 15039 | 150 | 39 | 2 | 3 | 4 | 6 | BoL
[8 empty] | 15040 | 150 | 40 | 2 | 3 | 4 | 6 | BoL
[8 empty] | 15041 | 150 | 41 | 2 | 3 | 4 | 6 | BoL
[8 empty] | 1603 | 160 | 3 | 1 | 1 | 1 | 1 | BoL
[8 empty] | 1604 | 160 | 4 | 1 | 1 | 1 | 1 | BoL
[8 empty] | 1605 | 160 | 5 | 1 | 1 | 1 | 1 | BoL
[8 empty] | 1606 | 160 | 6 | 1 | 1 | 1 | 1 | BoL
[8 empty] | 1607 | 160 | 7 | 1 | 1 | 1 | 1 | BoL
[8 empty] | 1608 | 160 | 8 | 1 | 1 | 1 | 2 | BoL
[8 empty] | 1609 | 160 | 9 | 1 | 1 | 1 | 2 | BoL
[8 empty] | 16010 | 160 | 10 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 16011 | 160 | 11 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 16012 | 160 | 12 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 16013 | 160 | 13 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 16014 | 160 | 14 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 16015 | 160 | 15 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 16016 | 160 | 16 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 16017 | 160 | 17 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 16018 | 160 | 18 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 16019 | 160 | 19 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 16020 | 160 | 20 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 16021 | 160 | 21 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 16022 | 160 | 22 | 1 | 2 | 3 | 3 | BoL
[8 empty] | 16023 | 160 | 23 | 1 | 2 | 3 | 3 | BoL
[8 empty] | 16024 | 160 | 24 | 1 | 2 | 3 | 3 | BoL
[8 empty] | 16025 | 160 | 25 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 16026 | 160 | 26 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 16027 | 160 | 27 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 16028 | 160 | 28 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 16029 | 160 | 29 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 16030 | 160 | 30 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 16031 | 160 | 31 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 16032 | 160 | 32 | 2 | 2 | 3 | 4 | BoL
[8 empty] | 16033 | 160 | 33 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 16034 | 160 | 34 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 16035 | 160 | 35 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 16036 | 160 | 36 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 16037 | 160 | 37 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 16038 | 160 | 38 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 16039 | 160 | 39 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 16040 | 160 | 40 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 16041 | 160 | 41 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 2003 | 200 | 3 | 1 | 1 | 1 | 1 | BoL
[8 empty] | 2004 | 200 | 4 | 1 | 1 | 1 | 1 | BoL
[8 empty] | 2005 | 200 | 5 | 1 | 1 | 1 | 2 | BoL
[8 empty] | 2006 | 200 | 6 | 1 | 1 | 1 | 2 | BoL
[8 empty] | 2007 | 200 | 7 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 2008 | 200 | 8 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 2009 | 200 | 9 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 20010 | 200 | 10 | 1 | 1 | 2 | 2 | BoL
[8 empty] | 20011 | 200 | 11 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 20012 | 200 | 12 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 20013 | 200 | 13 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 20014 | 200 | 14 | 1 | 2 | 2 | 3 | BoL
[8 empty] | 20015 | 200 | 15 | 1 | 2 | 3 | 3 | BoL
[8 empty] | 20016 | 200 | 16 | 1 | 2 | 3 | 3 | BoL
[8 empty] | 20017 | 200 | 17 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 20018 | 200 | 18 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 20019 | 200 | 19 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 20020 | 200 | 20 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 20021 | 200 | 21 | 1 | 2 | 3 | 4 | BoL
[8 empty] | 20022 | 200 | 22 | 2 | 2 | 3 | 4 | BoL
[8 empty] | 20023 | 200 | 23 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 20024 | 200 | 24 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 20025 | 200 | 25 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 20026 | 200 | 26 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 20027 | 200 | 27 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 20028 | 200 | 28 | 2 | 3 | 4 | 5 | BoL
[8 empty] | 20029 | 200 | 29 | 2 | 3 | 4 | 6 | BoL
[8 empty] | 20030 | 200 | 30 | 2 | 3 | 4 | 6 | BoL
[8 empty] | 20031 | 200 | 31 | 2 | 3 | 5 | 6 | BoL
[8 empty] | 20032 | 200 | 32 | 2 | 3 | 5 | 6 | BoL
[8 empty] | 20033 | 200 | 33 | 2 | 3 | 5 | 6 | BoL
[8 empty] | 20034 | 200 | 34 | 2 | 3 | 5 | 6 | BoL
[8 empty] | 20035 | 200 | 35 | 2 | 4 | 5 | 7 | BoL
[8 empty] | 20036 | 200 | 36 | 2 | 4 | 5 | 7 | BoL
[8 empty] | 20037 | 200 | 37 | 2 | 4 | 5 | 7 | BoL
[8 empty] | 20038 | 200 | 38 | 2 | 4 | 5 | 7 | BoL
[8 empty] | 20039 | 200 | 39 | 2 | 4 | 6 | 7 | BoL
[8 empty] | 20040 | 200 | 40 | 2 | 4 | 6 | 7 | BoL
[8 empty] | 20041 | 200 | 41 | 2 | 4 | 6 | 8 | BoL
|  |  | EoL | [7 empty] | BoL
| Rating | No. strings | 25 | 50 | 75 | 100 | Load [%] |  | Rating | No. strings | 25 | 50 | 75 | 100 | Load[%]
301 | 30 | 1 | 158.6 | 81.3 | 54 | 39.8 | [s] | 301 | 30 | 1 | 199.9 | 103.3 | 69 | 51.4 | [s]
401 | 40 | 1 | 101.9 | 51.9 | 34.3 | 25.1 | [s] | 401 | 40 | 1 | 128.7 | 66.3 | 44.2 | 32.7 | [s]
402 | 40 | 2 | NA | NA | NA | 52.5 | [s] | 402 | 40 | 2 | NA | NA | NA | 67 | [s]
501 | 50 | 1 | 70.8 | 35.9 | 23.5 | 17.1 | [s] | 501 | 50 | 1 | 89.8 | 46.1 | 30.6 | 22.6 | [s]
502 | 50 | 2 | NA | NA | 49 | 36.2 | [s] | 502 | 50 | 2 | NA | NA | NA | 46.6 | [s]
541 | 54 | 1 | 49.2 | 24.7 | 16 | 11.5 | [s] | 541 | 54 | 1 | 62.7 | 32 | 21.2 | 15.6 | [s]
542 | 54 | 2 | NA | 51.3 | 33.9 | 24.9 | [s] | 542 | 54 | 2 | NA | NA | 43.6 | 32.4 | [s]
543 | 54 | 3 | NA | NA | NA | 38.4 | [s] | 543 | 54 | 3 | NA | NA | NA | 49.2 | [s]
801 | 80 | 1 | 45.1 | 22.5 | 14.5 | 10.3 | [s] | 801 | 80 | 1 | 57.7 | 29.4 | 19.4 | 14.2 | [s]
802 | 80 | 2 | NA | 47.1 | 31 | 22.7 | [s] | 802 | 80 | 2 | NA | 60.1 | 40.1 | 29.7 | [s]
803 | 80 | 3 | NA | NA | NA | 35.2 | [s] | 803 | 80 | 3 | NA | NA | 60.8 | 45.3 | [s]
804 | 80 | 4 | NA | NA | NA | 47.6 | [s] | 804 | 80 | 4 | NA | NA | NA | 60.8 | [s]
1001 | 100 | 1 | 34.4 | 16.9 | 10.7 | 7.5 | [s] | 1001 | 100 | 1 | 44.2 | 22.4 | 14.7 | 10.7 | [s]
1002 | 100 | 2 | NA | 35.9 | 23.5 | 17.1 | [s] | 1002 | 100 | 2 | NA | 46.1 | 30.6 | 22.6 | [s]
1003 | 100 | 3 | NA | NA | 36.3 | 26.7 | [s] | 1003 | 100 | 3 | NA | NA | 46.6 | 34.6 | [s]
1004 | 100 | 4 | NA | NA | NA | 36.3 | [s] | 1004 | 100 | 4 | NA | NA | NA | 46.6 | [s]
1005 | 100 | 5 | NA | NA | NA | 45.9 | [s] | 1005 | 100 | 5 | NA | NA | NA | 58.6 | [s]
1006 | 100 | 6 | NA | NA | NA | 55.4 | [s] | 1006 | 100 | 6 | NA | NA | NA | 70.6 | [s]
1201 | 120 | 1 | 29.4 | 14.3 | 8.9 | 6.2 | [s] | 1201 | 120 | 1 | 38 | 19.1 | 12.5 | 9 | [s]
1202 | 120 | 2 | 60.9 | 30.7 | 20 | 14.5 | [s] | 1202 | 120 | 2 | 77.4 | 39.6 | 26.3 | 19.4 | [s]
1203 | 120 | 3 | NA | NA | 31 | 22.7 | [s] | 1203 | 120 | 3 | NA | 60.1 | 40.1 | 29.7 | [s]
1204 | 120 | 4 | NA | NA | 42.1 | 31 | [s] | 1204 | 120 | 4 | NA | NA | 53.9 | 40.1 | [s]
1205 | 120 | 5 | NA | NA | NA | 39.3 | [s] | 1205 | 120 | 5 | NA | NA |  | 50.4 | [s]
1501 | 150 | 1 | 22.2 | 10.6 | 6.5 | 4.3 | [s] | 1501 | 150 | 1 | 29 | 14.5 | 9.3 | 6.7 | [s]
1502 | 150 | 2 | 46.5 | 23.2 | 15 | 10.1 | [s] | 1502 | 150 | 2 | 59.4 | 30.3 | 20.1 | 14.7 | [s]
1503 | 150 | 3 | NA | 35.9 | 23.5 | 17.1 | [s] | 1503 | 150 | 3 | NA | 46.1 | 30.6 | 22.6 | [s]
1504 | 150 | 4 | NA | NA | 32 | 23.5 | [s] | 1504 | 150 | 4 | NA | NA | 41.3 | 30.6 | [s]
1505 | 150 | 5 | NA | NA | NA | 29.9 | [s] | 1505 | 150 | 5 | NA | NA | NA | 38.6 | [s]
1506 | 150 | 6 | NA | NA | NA | 36.3 | [s] | 1506 | 150 | 6 | NA | NA | NA | 46.6 | [s]
1601 | 160 | 1 | 23.8 | 11.3 | 6.9 | 4.6 | [s] | 1601 | 160 | 1 | 31.1 | 15.5 | 10 | 7.1 | [s]
1602 | 160 | 2 | 49.8 | 24.8 | 16 | 11.4 | [s] | 1602 | 160 | 2 | 63.6 | 32.4 | 21.4 | 15.7 | [s]
1603 | 160 | 3 | NA | 38.4 | 25.1 | 18.3 | [s] | 1603 | 160 | 3 | NA | 49.4 | 32.8 | 24.2 | [s]
1604 | 160 | 4 | NA | NA | 34.3 | 25.1 | [s] | 1604 | 160 | 4 | NA | NA | 44.2 | 32.8 | [s]
1605 | 160 | 5 | NA | NA | 43.4 | 32 | [s] | 1605 | 160 | 5 | NA | NA | NA | 41.4 | [s]
1606 | 160 | 6 | NA | NA | NA | 38.8 | [s] | 1606 | 160 | 6 | NA | NA | NA | 49.9 | [s]
2001 | 200 | 1 | 16.1 | 7.4 | 4.3 | 2.8 | [s] | 2001 | 200 | 1 | 21.5 | 10.5 | 6.7 | 4.7 | [s]
2002 | 200 | 2 | 34.4 | 16.9 | 10.7 | 7.5 | [s] | 2002 | 200 | 2 | 44.2 | 22.4 | 14.7 | 10.7 | [s]
2003 | 200 | 3 | NA | 26.4 | 17.1 | 12.3 | [s] | 2003 | 200 | 3 | NA | 34.2 | 22.6 | 16.6 | [s]
2004 | 200 | 4 | NA | 35.8 | 23.5 | 17.1 | [s] | 2004 | 200 | 4 | NA | 46.1 | 30.6 | 22.6 | [s]
2005 | 200 | 5 | NA | NA | 29.9 | 21.9 | [s] | 2005 | 200 | 5 | NA | NA | 38.6 | 28.6 | [s]
2006 | 200 | 6 | NA | NA | 36.3 | 26.7 | [s] | 2006 | 200 | 6 | NA | NA | 46.6 | 34.6 | [s]
2007 | 200 | 7 | NA | NA | NA | 31.5 | [s] | 2007 | 200 | 7 | NA | NA | NA | 40.6 | [s]

## 100% Load
100% Load | 93PM-30kW | 93PM-40kW | 93PM-50kW | 93PM-54kW | 93PM-80kW | 93PM-100kW | 93PM-120kW | 93PM-150kW | 93PM-160kW | 93PM-200kW
Autonomy time (sec.) | Strings required at End of Life (-20% capacity, -50% power)
3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2
4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2
5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2
6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2
7 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2
8 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3
9 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3
10 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3
11 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 2 | 3
12 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 3
13 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 4
14 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 4
15 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4
16 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4
17 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4
18 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 3 | 5
19 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 5
20 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 5
21 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 5
22 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 6
23 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 4 | 6
24 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 5 | 4 | 6
25 | 1 | 1 | 2 | 3 | 3 | 3 | 4 | 5 | 4 | 6
26 | 1 | 2 | 2 | 3 | 3 | 3 | 4 | 5 | 5 | 6
27 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5 | 7
28 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5 | 7
29 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5 | 7
30 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 6 | 5 | 7
Estimated Life | 20 years @30C
12 years @35C
8 years @40C
Autonomy time (sec.) | Strings required at Day1
3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2
6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2
7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2
8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2
9 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2
10 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2
11 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3
12 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3
13 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3
14 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3
15 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 2 | 3
16 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 3
17 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 4
18 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 4
19 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 4
20 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4
21 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4
22 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4
23 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 3 | 5
24 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 3 | 5
25 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 5
26 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 5
27 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 5
28 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 5
29 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 6
30 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 4 | 6
31 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 5 | 4 | 6
32 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 5 | 4 | 6
33 | 1 | 2 | 2 | 3 | 3 | 3 | 4 | 5 | 5 | 6
34 | 1 | 2 | 2 | 3 | 3 | 3 | 4 | 5 | 5 | 6
35 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5 | 7
36 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5 | 7
37 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5 | 7
38 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5 | 7
39 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 6 | 5 | 7
40 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 6 | 5 | 7
41 | 1 | 2 | 2 | 3 | 3 | 4 | 5 | 6 | 5 | 8
Estimated Life | 20 years @30C
12 years @35C
8 years @40C

## 93PM-30kW
93PM-30kW |  |  |  |  | 93PM-30kW
Load | 25% | 50% | 75% | 100% | Load | 25% | 50% | 75% | 100%
| 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Time 1 string, EOL (80%, 200%) | 158.6 | 81.3 | 54 | 39.8 | Time 1 string, BOL (100%, 100%) | 199.9 | 103.3 | 69 | 51.4
Autonomy time (sec.) | Strings required at End of Life (-20% capacity, -50% power) |  |  |  | Autonomy time (sec.) | Strings required at Day1
3 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 1 | 6 | 1 | 1 | 1 | 1
7 | 1 | 1 | 1 | 1 | 7 | 1 | 1 | 1 | 1
8 | 1 | 1 | 1 | 1 | 8 | 1 | 1 | 1 | 1
9 | 1 | 1 | 1 | 1 | 9 | 1 | 1 | 1 | 1
10 | 1 | 1 | 1 | 1 | 10 | 1 | 1 | 1 | 1
11 | 1 | 1 | 1 | 1 | 11 | 1 | 1 | 1 | 1
12 | 1 | 1 | 1 | 1 | 12 | 1 | 1 | 1 | 1
13 | 1 | 1 | 1 | 1 | 13 | 1 | 1 | 1 | 1
14 | 1 | 1 | 1 | 1 | 14 | 1 | 1 | 1 | 1
15 | 1 | 1 | 1 | 1 | 15 | 1 | 1 | 1 | 1
16 | 1 | 1 | 1 | 1 | 16 | 1 | 1 | 1 | 1
17 | 1 | 1 | 1 | 1 | 17 | 1 | 1 | 1 | 1
18 | 1 | 1 | 1 | 1 | 18 | 1 | 1 | 1 | 1
19 | 1 | 1 | 1 | 1 | 19 | 1 | 1 | 1 | 1
20 | 1 | 1 | 1 | 1 | 20 | 1 | 1 | 1 | 1
21 | 1 | 1 | 1 | 1 | 21 | 1 | 1 | 1 | 1
22 | 1 | 1 | 1 | 1 | 22 | 1 | 1 | 1 | 1
23 | 1 | 1 | 1 | 1 | 23 | 1 | 1 | 1 | 1
24 | 1 | 1 | 1 | 1 | 24 | 1 | 1 | 1 | 1
25 | 1 | 1 | 1 | 1 | 25 | 1 | 1 | 1 | 1
26 | 1 | 1 | 1 | 1 | 26 | 1 | 1 | 1 | 1
27 | 1 | 1 | 1 | 1 | 27 | 1 | 1 | 1 | 1
28 | 1 | 1 | 1 | 1 | 28 | 1 | 1 | 1 | 1
29 | 1 | 1 | 1 | 1 | 29 | 1 | 1 | 1 | 1
30 | 1 | 1 | 1 | 1 | 30 | 1 | 1 | 1 | 1
Estimated Life | 20 years @30C |  |  |  | 31 | 1 | 1 | 1 | 1
| 12 years @35C |  |  |  | 32 | 1 | 1 | 1 | 1
| 8 years @40C |  |  |  | 33 | 1 | 1 | 1 | 1
[5 empty] | 34 | 1 | 1 | 1 | 1
[5 empty] | 35 | 1 | 1 | 1 | 1
[5 empty] | 36 | 1 | 1 | 1 | 1
[5 empty] | 37 | 1 | 1 | 1 | 1
[5 empty] | 38 | 1 | 1 | 1 | 1
[5 empty] | 39 | 1 | 1 | 1 | 1
[5 empty] | 40 | 1 | 1 | 1 | 1
[5 empty] | 41 | 1 | 1 | 1 | 1

## 93PM-40kW
93PM-40kW |  |  |  |  | 93PM-40kW
Load | 25% | 50% | 75% | 100% | Load | 25% | 50% | 75% | 100%
Autonomy time (sec.) | Strings required at End of Life (-20% capacity, -50% power) |  |  |  | Autonomy time (sec.) | Strings required at Day1
3 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 1 | 6 | 1 | 1 | 1 | 1
7 | 1 | 1 | 1 | 1 | 7 | 1 | 1 | 1 | 1
8 | 1 | 1 | 1 | 1 | 8 | 1 | 1 | 1 | 1
9 | 1 | 1 | 1 | 1 | 9 | 1 | 1 | 1 | 1
10 | 1 | 1 | 1 | 1 | 10 | 1 | 1 | 1 | 1
11 | 1 | 1 | 1 | 1 | 11 | 1 | 1 | 1 | 1
12 | 1 | 1 | 1 | 1 | 12 | 1 | 1 | 1 | 1
13 | 1 | 1 | 1 | 1 | 13 | 1 | 1 | 1 | 1
14 | 1 | 1 | 1 | 1 | 14 | 1 | 1 | 1 | 1
15 | 1 | 1 | 1 | 1 | 15 | 1 | 1 | 1 | 1
16 | 1 | 1 | 1 | 1 | 16 | 1 | 1 | 1 | 1
17 | 1 | 1 | 1 | 1 | 17 | 1 | 1 | 1 | 1
18 | 1 | 1 | 1 | 1 | 18 | 1 | 1 | 1 | 1
19 | 1 | 1 | 1 | 1 | 19 | 1 | 1 | 1 | 1
20 | 1 | 1 | 1 | 1 | 20 | 1 | 1 | 1 | 1
21 | 1 | 1 | 1 | 1 | 21 | 1 | 1 | 1 | 1
22 | 1 | 1 | 1 | 1 | 22 | 1 | 1 | 1 | 1
23 | 1 | 1 | 1 | 1 | 23 | 1 | 1 | 1 | 1
24 | 1 | 1 | 1 | 1 | 24 | 1 | 1 | 1 | 1
25 | 1 | 1 | 1 | 1 | 25 | 1 | 1 | 1 | 1
26 | 1 | 1 | 1 | 2 | 26 | 1 | 1 | 1 | 1
27 | 1 | 1 | 1 | 2 | 27 | 1 | 1 | 1 | 1
28 | 1 | 1 | 1 | 2 | 28 | 1 | 1 | 1 | 1
29 | 1 | 1 | 1 | 2 | 29 | 1 | 1 | 1 | 1
30 | 1 | 1 | 1 | 2 | 30 | 1 | 1 | 1 | 1
Estimated Life | 20 years @30C |  |  |  | 31 | 1 | 1 | 1 | 1
| 12 years @35C |  |  |  | 32 | 1 | 1 | 1 | 1
| 8 years @40C |  |  |  | 33 | 1 | 1 | 1 | 2
[5 empty] | 34 | 1 | 1 | 1 | 2
[5 empty] | 35 | 1 | 1 | 1 | 2
[5 empty] | 36 | 1 | 1 | 1 | 2
[5 empty] | 37 | 1 | 1 | 1 | 2
[5 empty] | 38 | 1 | 1 | 1 | 2
[5 empty] | 39 | 1 | 1 | 1 | 2
[5 empty] | 40 | 1 | 1 | 1 | 2
[5 empty] | 41 | 1 | 1 | 1 | 2

## 93PM-50kW
93PM-50kW |  |  |  |  | 93PM-50kW
Load | 25% | 50% | 75% | 10000% | Load | 25% | 50% | 75% | 10000%
Autonomy time (sec.) | Strings required at End of Life (-20% capacity, -50% power) |  |  |  | Autonomy time (sec.) | Strings required at Day1
3 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 1 | 6 | 1 | 1 | 1 | 1
7 | 1 | 1 | 1 | 1 | 7 | 1 | 1 | 1 | 1
8 | 1 | 1 | 1 | 1 | 8 | 1 | 1 | 1 | 1
9 | 1 | 1 | 1 | 1 | 9 | 1 | 1 | 1 | 1
10 | 1 | 1 | 1 | 1 | 10 | 1 | 1 | 1 | 1
11 | 1 | 1 | 1 | 1 | 11 | 1 | 1 | 1 | 1
12 | 1 | 1 | 1 | 1 | 12 | 1 | 1 | 1 | 1
13 | 1 | 1 | 1 | 1 | 13 | 1 | 1 | 1 | 1
14 | 1 | 1 | 1 | 1 | 14 | 1 | 1 | 1 | 1
15 | 1 | 1 | 1 | 1 | 15 | 1 | 1 | 1 | 1
16 | 1 | 1 | 1 | 1 | 16 | 1 | 1 | 1 | 1
17 | 1 | 1 | 1 | 1 | 17 | 1 | 1 | 1 | 1
18 | 1 | 1 | 1 | 2 | 18 | 1 | 1 | 1 | 1
19 | 1 | 1 | 1 | 2 | 19 | 1 | 1 | 1 | 1
20 | 1 | 1 | 1 | 2 | 20 | 1 | 1 | 1 | 1
21 | 1 | 1 | 1 | 2 | 21 | 1 | 1 | 1 | 1
22 | 1 | 1 | 1 | 2 | 22 | 1 | 1 | 1 | 1
23 | 1 | 1 | 1 | 2 | 23 | 1 | 1 | 1 | 2
24 | 1 | 1 | 2 | 2 | 24 | 1 | 1 | 1 | 2
25 | 1 | 1 | 2 | 2 | 25 | 1 | 1 | 1 | 2
26 | 1 | 1 | 2 | 2 | 26 | 1 | 1 | 1 | 2
27 | 1 | 1 | 2 | 2 | 27 | 1 | 1 | 1 | 2
28 | 1 | 1 | 2 | 2 | 28 | 1 | 1 | 1 | 2
29 | 1 | 1 | 2 | 2 | 29 | 1 | 1 | 1 | 2
30 | 1 | 1 | 2 | 2 | 30 | 1 | 1 | 1 | 2
Estimated Life | 20 years @30C |  |  |  | 31 | 1 | 1 | 2 | 2
| 12 years @35C |  |  |  | 32 | 1 | 1 | 2 | 2
| 8 years @40C |  |  |  | 33 | 1 | 1 | 2 | 2
[5 empty] | 34 | 1 | 1 | 2 | 2
[5 empty] | 35 | 1 | 1 | 2 | 2
[5 empty] | 36 | 1 | 1 | 2 | 2
[5 empty] | 37 | 1 | 1 | 2 | 2
[5 empty] | 38 | 1 | 1 | 2 | 2
[5 empty] | 39 | 1 | 1 | 2 | 2
[5 empty] | 40 | 1 | 1 | 2 | 2
[5 empty] | 41 | 1 | 1 | 2 | 2

## 93PM-54kW
93PM-54kW |  |  |  |  | 93PM-54kW
Load | 25% | 50% | 75% | 100% | Load | 25% | 50% | 75% | 100%
Autonomy time (sec.) | Strings required at End of Life (-20% capacity, -50% power) |  |  |  | Autonomy time (sec.) | Strings required at Day1
3 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 1 | 6 | 1 | 1 | 1 | 1
7 | 1 | 1 | 1 | 1 | 7 | 1 | 1 | 1 | 1
8 | 1 | 1 | 1 | 1 | 8 | 1 | 1 | 1 | 1
9 | 1 | 1 | 1 | 1 | 9 | 1 | 1 | 1 | 1
10 | 1 | 1 | 1 | 1 | 10 | 1 | 1 | 1 | 1
11 | 1 | 1 | 1 | 1 | 11 | 1 | 1 | 1 | 1
12 | 1 | 1 | 1 | 2 | 12 | 1 | 1 | 1 | 1
13 | 1 | 1 | 1 | 2 | 13 | 1 | 1 | 1 | 1
14 | 1 | 1 | 1 | 2 | 14 | 1 | 1 | 1 | 1
15 | 1 | 1 | 1 | 2 | 15 | 1 | 1 | 1 | 1
16 | 1 | 1 | 2 | 2 | 16 | 1 | 1 | 1 | 2
17 | 1 | 1 | 2 | 2 | 17 | 1 | 1 | 1 | 2
18 | 1 | 1 | 2 | 2 | 18 | 1 | 1 | 1 | 2
19 | 1 | 1 | 2 | 2 | 19 | 1 | 1 | 1 | 2
20 | 1 | 1 | 2 | 2 | 20 | 1 | 1 | 1 | 2
21 | 1 | 1 | 2 | 2 | 21 | 1 | 1 | 1 | 2
22 | 1 | 1 | 2 | 2 | 22 | 1 | 1 | 2 | 2
23 | 1 | 1 | 2 | 2 | 23 | 1 | 1 | 2 | 2
24 | 1 | 1 | 2 | 2 | 24 | 1 | 1 | 2 | 2
25 | 1 | 2 | 2 | 3 | 25 | 1 | 1 | 2 | 2
26 | 1 | 2 | 2 | 3 | 26 | 1 | 1 | 2 | 2
27 | 1 | 2 | 2 | 3 | 27 | 1 | 1 | 2 | 2
28 | 1 | 2 | 2 | 3 | 28 | 1 | 1 | 2 | 2
29 | 1 | 2 | 2 | 3 | 29 | 1 | 1 | 2 | 2
30 | 1 | 2 | 2 | 3 | 30 | 1 | 1 | 2 | 2
Estimated Life | 20 years @30C |  |  |  | 31 | 1 | 1 | 2 | 2
| 12 years @35C |  |  |  | 32 | 1 | 2 | 2 | 2
| 8 years @40C |  |  |  | 33 | 1 | 2 | 2 | 3
[5 empty] | 34 | 1 | 2 | 2 | 3
[5 empty] | 35 | 1 | 2 | 2 | 3
[5 empty] | 36 | 1 | 2 | 2 | 3
[5 empty] | 37 | 1 | 2 | 2 | 3
[5 empty] | 38 | 1 | 2 | 2 | 3
[5 empty] | 39 | 1 | 2 | 2 | 3
[5 empty] | 40 | 1 | 2 | 2 | 3
[5 empty] | 41 | 1 | 2 | 2 | 3

## 93PM-80kW
93PM-80kW |  |  |  |  | 93PM-80kW
Load | 25% | 50% | 75% | 100% | Load | 25% | 50% | 75% | 100%
Autonomy time (sec.) | Strings required at End of Life (-20% capacity, -50% power) |  |  |  | Autonomy time (sec.) | Strings required at Day1
3 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 1 | 6 | 1 | 1 | 1 | 1
7 | 1 | 1 | 1 | 1 | 7 | 1 | 1 | 1 | 1
8 | 1 | 1 | 1 | 1 | 8 | 1 | 1 | 1 | 1
9 | 1 | 1 | 1 | 1 | 9 | 1 | 1 | 1 | 1
10 | 1 | 1 | 1 | 1 | 10 | 1 | 1 | 1 | 1
11 | 1 | 1 | 1 | 2 | 11 | 1 | 1 | 1 | 1
12 | 1 | 1 | 1 | 2 | 12 | 1 | 1 | 1 | 1
13 | 1 | 1 | 1 | 2 | 13 | 1 | 1 | 1 | 1
14 | 1 | 1 | 1 | 2 | 14 | 1 | 1 | 1 | 1
15 | 1 | 1 | 2 | 2 | 15 | 1 | 1 | 1 | 2
16 | 1 | 1 | 2 | 2 | 16 | 1 | 1 | 1 | 2
17 | 1 | 1 | 2 | 2 | 17 | 1 | 1 | 1 | 2
18 | 1 | 1 | 2 | 2 | 18 | 1 | 1 | 1 | 2
19 | 1 | 1 | 2 | 2 | 19 | 1 | 1 | 1 | 2
20 | 1 | 1 | 2 | 2 | 20 | 1 | 1 | 2 | 2
21 | 1 | 1 | 2 | 2 | 21 | 1 | 1 | 2 | 2
22 | 1 | 1 | 2 | 2 | 22 | 1 | 1 | 2 | 2
23 | 1 | 2 | 2 | 3 | 23 | 1 | 1 | 2 | 2
24 | 1 | 2 | 2 | 3 | 24 | 1 | 1 | 2 | 2
25 | 1 | 2 | 2 | 3 | 25 | 1 | 1 | 2 | 2
26 | 1 | 2 | 2 | 3 | 26 | 1 | 1 | 2 | 2
27 | 1 | 2 | 2 | 3 | 27 | 1 | 1 | 2 | 2
28 | 1 | 2 | 2 | 3 | 28 | 1 | 1 | 2 | 2
29 | 1 | 2 | 2 | 3 | 29 | 1 | 1 | 2 | 2
30 | 1 | 2 | 2 | 3 | 30 | 1 | 2 | 2 | 3
Estimated Life | 20 years @30C |  |  |  | 31 | 1 | 2 | 2 | 3
| 12 years @35C |  |  |  | 32 | 1 | 2 | 2 | 3
| 8 years @40C |  |  |  | 33 | 1 | 2 | 2 | 3
[5 empty] | 34 | 1 | 2 | 2 | 3
[5 empty] | 35 | 1 | 2 | 2 | 3
[5 empty] | 36 | 1 | 2 | 2 | 3
[5 empty] | 37 | 1 | 2 | 2 | 3
[5 empty] | 38 | 1 | 2 | 2 | 3
[5 empty] | 39 | 1 | 2 | 2 | 3
[5 empty] | 40 | 1 | 2 | 2 | 3
[5 empty] | 41 | 1 | 2 | 3 | 3

## 93PM-100kW
93PM-100kW |  |  |  |  | 93PM-100kW
Load | 25% | 50% | 75% | 100% | Load | 25% | 50% | 75% | 100%
Autonomy time (sec.) | Strings required at End of Life (-20% capacity, -50% power) |  |  |  | Autonomy time (sec.) | Strings required at Day1
3 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 1 | 6 | 1 | 1 | 1 | 1
7 | 1 | 1 | 1 | 1 | 7 | 1 | 1 | 1 | 1
8 | 1 | 1 | 1 | 2 | 8 | 1 | 1 | 1 | 1
9 | 1 | 1 | 1 | 2 | 9 | 1 | 1 | 1 | 1
10 | 1 | 1 | 1 | 2 | 10 | 1 | 1 | 1 | 1
11 | 1 | 1 | 2 | 2 | 11 | 1 | 1 | 1 | 2
12 | 1 | 1 | 2 | 2 | 12 | 1 | 1 | 1 | 2
13 | 1 | 1 | 2 | 2 | 13 | 1 | 1 | 1 | 2
14 | 1 | 1 | 2 | 2 | 14 | 1 | 1 | 1 | 2
15 | 1 | 1 | 2 | 2 | 15 | 1 | 1 | 2 | 2
16 | 1 | 1 | 2 | 2 | 16 | 1 | 1 | 2 | 2
17 | 1 | 2 | 2 | 2 | 17 | 1 | 1 | 2 | 2
18 | 1 | 2 | 2 | 3 | 18 | 1 | 1 | 2 | 2
19 | 1 | 2 | 2 | 3 | 19 | 1 | 1 | 2 | 2
20 | 1 | 2 | 2 | 3 | 20 | 1 | 1 | 2 | 2
21 | 1 | 2 | 2 | 3 | 21 | 1 | 1 | 2 | 2
22 | 1 | 2 | 2 | 3 | 22 | 1 | 1 | 2 | 2
23 | 1 | 2 | 2 | 3 | 23 | 1 | 2 | 2 | 3
24 | 1 | 2 | 3 | 3 | 24 | 1 | 2 | 2 | 3
25 | 1 | 2 | 3 | 3 | 25 | 1 | 2 | 2 | 3
26 | 1 | 2 | 3 | 3 | 26 | 1 | 2 | 2 | 3
27 | 1 | 2 | 3 | 4 | 27 | 1 | 2 | 2 | 3
28 | 1 | 2 | 3 | 4 | 28 | 1 | 2 | 2 | 3
29 | 1 | 2 | 3 | 4 | 29 | 1 | 2 | 2 | 3
30 | 1 | 2 | 3 | 4 | 30 | 1 | 2 | 2 | 3
Estimated Life | 20 years @30C |  |  |  | 31 | 1 | 2 | 3 | 3
| 12 years @35C |  |  |  | 32 | 1 | 2 | 3 | 3
| 8 years @40C |  |  |  | 33 | 1 | 2 | 3 | 3
[5 empty] | 34 | 1 | 2 | 3 | 3
[5 empty] | 35 | 1 | 2 | 3 | 4
[5 empty] | 36 | 1 | 2 | 3 | 4
[5 empty] | 37 | 1 | 2 | 3 | 4
[5 empty] | 38 | 1 | 2 | 3 | 4
[5 empty] | 39 | 1 | 2 | 3 | 4
[5 empty] | 40 | 1 | 2 | 3 | 4
[5 empty] | 41 | 1 | 2 | 3 | 4

## 93PM-120kW
93PM-120kW |  |  |  |  | 93PM-120kW
Load | 25% | 50% | 75% | 100% | Load | 25% | 50% | 75% | 100%
Autonomy time (sec.) | Strings required at End of Life (-20% capacity, -50% power) |  |  |  | Autonomy time (sec.) | Strings required at Day1
3 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 1 | 6 | 1 | 1 | 1 | 1
7 | 1 | 1 | 1 | 2 | 7 | 1 | 1 | 1 | 1
8 | 1 | 1 | 1 | 2 | 8 | 1 | 1 | 1 | 1
9 | 1 | 1 | 2 | 2 | 9 | 1 | 1 | 1 | 2
10 | 1 | 1 | 2 | 2 | 10 | 1 | 1 | 1 | 2
11 | 1 | 1 | 2 | 2 | 11 | 1 | 1 | 1 | 2
12 | 1 | 1 | 2 | 2 | 12 | 1 | 1 | 1 | 2
13 | 1 | 1 | 2 | 2 | 13 | 1 | 1 | 2 | 2
14 | 1 | 1 | 2 | 2 | 14 | 1 | 1 | 2 | 2
15 | 1 | 2 | 2 | 3 | 15 | 1 | 1 | 2 | 2
16 | 1 | 2 | 2 | 3 | 16 | 1 | 1 | 2 | 2
17 | 1 | 2 | 2 | 3 | 17 | 1 | 1 | 2 | 2
18 | 1 | 2 | 2 | 3 | 18 | 1 | 1 | 2 | 2
19 | 1 | 2 | 2 | 3 | 19 | 1 | 1 | 2 | 2
20 | 1 | 2 | 3 | 3 | 20 | 1 | 2 | 2 | 3
21 | 1 | 2 | 3 | 3 | 21 | 1 | 2 | 2 | 3
22 | 1 | 2 | 3 | 3 | 22 | 1 | 2 | 2 | 3
23 | 1 | 2 | 3 | 4 | 23 | 1 | 2 | 2 | 3
24 | 1 | 2 | 3 | 4 | 24 | 1 | 2 | 2 | 3
25 | 1 | 2 | 3 | 4 | 25 | 1 | 2 | 2 | 3
26 | 1 | 2 | 3 | 4 | 26 | 1 | 2 | 2 | 3
27 | 1 | 2 | 3 | 4 | 27 | 1 | 2 | 3 | 3
28 | 1 | 2 | 3 | 4 | 28 | 1 | 2 | 3 | 3
29 | 1 | 2 | 3 | 4 | 29 | 1 | 2 | 3 | 3
30 | 2 | 2 | 3 | 4 | 30 | 1 | 2 | 3 | 4
Estimated Life | 20 years @30C |  |  |  | 31 | 1 | 2 | 3 | 4
| 12 years @35C |  |  |  | 32 | 1 | 2 | 3 | 4
| 8 years @40C |  |  |  | 33 | 1 | 2 | 3 | 4
[5 empty] | 34 | 1 | 2 | 3 | 4
[5 empty] | 35 | 1 | 2 | 3 | 4
[5 empty] | 36 | 1 | 2 | 3 | 4
[5 empty] | 37 | 1 | 2 | 3 | 4
[5 empty] | 38 | 2 | 2 | 3 | 4
[5 empty] | 39 | 2 | 2 | 3 | 4
[5 empty] | 40 | 2 | 3 | 3 | 4
[5 empty] | 41 | 2 | 3 | 4 | 5

## 93PM-150kW
93PM-150kW |  |  |  |  | 93PM-150kW
Load | 25% | 50% | 75% | 100% | Load | 25% | 50% | 75% | 100%
Autonomy time (sec.) | Strings required at End of Life (-20% capacity, -50% power) |  |  |  | Autonomy time (sec.) | Strings required at Day1
3 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 2 | 5 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 2 | 6 | 1 | 1 | 1 | 1
7 | 1 | 1 | 2 | 2 | 7 | 1 | 1 | 1 | 2
8 | 1 | 1 | 2 | 2 | 8 | 1 | 1 | 1 | 2
9 | 1 | 1 | 2 | 2 | 9 | 1 | 1 | 1 | 2
10 | 1 | 1 | 2 | 2 | 10 | 1 | 1 | 2 | 2
11 | 1 | 2 | 2 | 3 | 11 | 1 | 1 | 2 | 2
12 | 1 | 2 | 2 | 3 | 12 | 1 | 1 | 2 | 2
13 | 1 | 2 | 2 | 3 | 13 | 1 | 1 | 2 | 2
14 | 1 | 2 | 2 | 3 | 14 | 1 | 1 | 2 | 2
15 | 1 | 2 | 3 | 3 | 15 | 1 | 2 | 2 | 3
16 | 1 | 2 | 3 | 3 | 16 | 1 | 2 | 2 | 3
17 | 1 | 2 | 3 | 3 | 17 | 1 | 2 | 2 | 3
18 | 1 | 2 | 3 | 4 | 18 | 1 | 2 | 2 | 3
19 | 1 | 2 | 3 | 4 | 19 | 1 | 2 | 2 | 3
20 | 1 | 2 | 3 | 4 | 20 | 1 | 2 | 2 | 3
21 | 1 | 2 | 3 | 4 | 21 | 1 | 2 | 3 | 3
22 | 1 | 2 | 3 | 4 | 22 | 1 | 2 | 3 | 3
23 | 2 | 2 | 3 | 4 | 23 | 1 | 2 | 3 | 4
24 | 2 | 3 | 4 | 5 | 24 | 1 | 2 | 3 | 4
25 | 2 | 3 | 4 | 5 | 25 | 1 | 2 | 3 | 4
26 | 2 | 3 | 4 | 5 | 26 | 1 | 2 | 3 | 4
27 | 2 | 3 | 4 | 5 | 27 | 1 | 2 | 3 | 4
28 | 2 | 3 | 4 | 5 | 28 | 1 | 2 | 3 | 4
29 | 2 | 3 | 4 | 5 | 29 | 2 | 2 | 3 | 4
30 | 2 | 3 | 4 | 6 | 30 | 2 | 2 | 3 | 4
Estimated Life | 20 years @30C |  |  |  | 31 | 2 | 3 | 4 | 5
| 12 years @35C |  |  |  | 32 | 2 | 3 | 4 | 5
| 8 years @40C |  |  |  | 33 | 2 | 3 | 4 | 5
[5 empty] | 34 | 2 | 3 | 4 | 5
[5 empty] | 35 | 2 | 3 | 4 | 5
[5 empty] | 36 | 2 | 3 | 4 | 5
[5 empty] | 37 | 2 | 3 | 4 | 5
[5 empty] | 38 | 2 | 3 | 4 | 5
[5 empty] | 39 | 2 | 3 | 4 | 6
[5 empty] | 40 | 2 | 3 | 4 | 6
[5 empty] | 41 | 2 | 3 | 4 | 6

## 93PM-160kW
93PM-160kW |  |  |  |  | 93PM-160kW
Load | 25% | 50% | 75% | 100% | Load | 25% | 50% | 75% | 100%
Autonomy time (sec.) | Strings required at End of Life (-20% capacity, -50% power) |  |  |  | Autonomy time (sec.) | Strings required at Day1
3 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 2 | 5 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 2 | 6 | 1 | 1 | 1 | 1
7 | 1 | 1 | 2 | 2 | 7 | 1 | 1 | 1 | 1
8 | 1 | 1 | 2 | 2 | 8 | 1 | 1 | 1 | 2
9 | 1 | 1 | 2 | 2 | 9 | 1 | 1 | 1 | 2
10 | 1 | 1 | 2 | 2 | 10 | 1 | 1 | 2 | 2
11 | 1 | 1 | 2 | 2 | 11 | 1 | 1 | 2 | 2
12 | 1 | 2 | 2 | 3 | 12 | 1 | 1 | 2 | 2
13 | 1 | 2 | 2 | 3 | 13 | 1 | 1 | 2 | 2
14 | 1 | 2 | 2 | 3 | 14 | 1 | 1 | 2 | 2
15 | 1 | 2 | 2 | 3 | 15 | 1 | 1 | 2 | 2
16 | 1 | 2 | 3 | 3 | 16 | 1 | 2 | 2 | 3
17 | 1 | 2 | 3 | 3 | 17 | 1 | 2 | 2 | 3
18 | 1 | 2 | 3 | 3 | 18 | 1 | 2 | 2 | 3
19 | 1 | 2 | 3 | 4 | 19 | 1 | 2 | 2 | 3
20 | 1 | 2 | 3 | 4 | 20 | 1 | 2 | 2 | 3
21 | 1 | 2 | 3 | 4 | 21 | 1 | 2 | 2 | 3
22 | 1 | 2 | 3 | 4 | 22 | 1 | 2 | 3 | 3
23 | 1 | 2 | 3 | 4 | 23 | 1 | 2 | 3 | 3
24 | 2 | 2 | 3 | 4 | 24 | 1 | 2 | 3 | 3
25 | 2 | 3 | 3 | 4 | 25 | 1 | 2 | 3 | 4
26 | 2 | 3 | 4 | 5 | 26 | 1 | 2 | 3 | 4
27 | 2 | 3 | 4 | 5 | 27 | 1 | 2 | 3 | 4
28 | 2 | 3 | 4 | 5 | 28 | 1 | 2 | 3 | 4
29 | 2 | 3 | 4 | 5 | 29 | 1 | 2 | 3 | 4
30 | 2 | 3 | 4 | 5 | 30 | 1 | 2 | 3 | 4
Estimated Life | 20 years @30C |  |  |  | 31 | 1 | 2 | 3 | 4
| 12 years @35C |  |  |  | 32 | 2 | 2 | 3 | 4
| 8 years @40C |  |  |  | 33 | 2 | 3 | 4 | 5
[5 empty] | 34 | 2 | 3 | 4 | 5
[5 empty] | 35 | 2 | 3 | 4 | 5
[5 empty] | 36 | 2 | 3 | 4 | 5
[5 empty] | 37 | 2 | 3 | 4 | 5
[5 empty] | 38 | 2 | 3 | 4 | 5
[5 empty] | 39 | 2 | 3 | 4 | 5
[5 empty] | 40 | 2 | 3 | 4 | 5
[5 empty] | 41 | 2 | 3 | 4 | 5

## 93PM-200kW
93PM-200kW |  |  |  |  | 93PM-200kW
Load | 25% | 50% | 75% | 100% | Load | 25% | 50% | 75% | 100%
Autonomy time (sec.) | Strings required at End of Life (-20% capacity, -50% power) |  |  |  | Autonomy time (sec.) | Strings required at Day1
3 | 1 | 1 | 1 | 2 | 3 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 2 | 4 | 1 | 1 | 1 | 1
5 | 1 | 1 | 2 | 2 | 5 | 1 | 1 | 1 | 2
6 | 1 | 1 | 2 | 2 | 6 | 1 | 1 | 1 | 2
7 | 1 | 1 | 2 | 2 | 7 | 1 | 1 | 2 | 2
8 | 1 | 2 | 2 | 3 | 8 | 1 | 1 | 2 | 2
9 | 1 | 2 | 2 | 3 | 9 | 1 | 1 | 2 | 2
10 | 1 | 2 | 2 | 3 | 10 | 1 | 1 | 2 | 2
11 | 1 | 2 | 3 | 3 | 11 | 1 | 2 | 2 | 3
12 | 1 | 2 | 3 | 3 | 12 | 1 | 2 | 2 | 3
13 | 1 | 2 | 3 | 4 | 13 | 1 | 2 | 2 | 3
14 | 1 | 2 | 3 | 4 | 14 | 1 | 2 | 2 | 3
15 | 1 | 2 | 3 | 4 | 15 | 1 | 2 | 3 | 3
16 | 1 | 2 | 3 | 4 | 16 | 1 | 2 | 3 | 3
17 | 2 | 3 | 3 | 4 | 17 | 1 | 2 | 3 | 4
18 | 2 | 3 | 4 | 5 | 18 | 1 | 2 | 3 | 4
19 | 2 | 3 | 4 | 5 | 19 | 1 | 2 | 3 | 4
20 | 2 | 3 | 4 | 5 | 20 | 1 | 2 | 3 | 4
21 | 2 | 3 | 4 | 5 | 21 | 1 | 2 | 3 | 4
22 | 2 | 3 | 4 | 6 | 22 | 2 | 2 | 3 | 4
23 | 2 | 3 | 4 | 6 | 23 | 2 | 3 | 4 | 5
24 | 2 | 3 | 5 | 6 | 24 | 2 | 3 | 4 | 5
25 | 2 | 3 | 5 | 6 | 25 | 2 | 3 | 4 | 5
26 | 2 | 3 | 5 | 6 | 26 | 2 | 3 | 4 | 5
27 | 2 | 4 | 5 | 7 | 27 | 2 | 3 | 4 | 5
28 | 2 | 4 | 5 | 7 | 28 | 2 | 3 | 4 | 5
29 | 2 | 4 | 5 | 7 | 29 | 2 | 3 | 4 | 6
30 | 2 | 4 | 6 | 7 | 30 | 2 | 3 | 4 | 6
Estimated Life | 20 years @30C |  |  |  | 31 | 2 | 3 | 5 | 6
| 12 years @35C |  |  |  | 32 | 2 | 3 | 5 | 6
| 8 years @40C |  |  |  | 33 | 2 | 3 | 5 | 6
[5 empty] | 34 | 2 | 3 | 5 | 6
[5 empty] | 35 | 2 | 4 | 5 | 7
[5 empty] | 36 | 2 | 4 | 5 | 7
[5 empty] | 37 | 2 | 4 | 5 | 7
[5 empty] | 38 | 2 | 4 | 5 | 7
[5 empty] | 39 | 2 | 4 | 6 | 7
[5 empty] | 40 | 2 | 4 | 6 | 7
[5 empty] | 41 | 2 | 4 | 6 | 8